SECTION 230516 – EXPANSION FITTINGS AND LOOPS FOR HVAC PIPING

First Edition 5-16-2017

(Engineer shall edit specifications and blue text in header to meet project requirements. This includes but is not limited to updating Equipment and/or Material Model Numbers indicated in the specifications and adding any additional specifications that may be required by the project. Also turn off all “Underlines”.)

GENERAL

RELATED DOCUMENTS

- Drawings and general provisions of Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this section and all other sections of Division 23.

SUMMARY

This section includes the requirements for expansion fittings, and loops using the following:

Metal-bellows packless expansion joints.

Rubber packless expansion joints.

Alignment guides and anchors.

PERFORMANCE REQUIREMENTS

Compatibility:  Products shall be suitable for piping service fluids, materials, working pressures, and temperatures.

Capability:  Products to absorb 200% of maximum axial movement between anchors.

ACTION SUBMITTALS

Product Data:  For each specified product, include manufacturers cut sheets, dimensional data, performance data, installation instructions, specified options, and warranty information.

Delegated-Design Submittal: For each anchor and alignment guide indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation. < Delete paragraph ‘B’ if not required>

Design Calculations: Calculate requirements for thermal expansion of piping systems and for selecting and designing expansion joints, loops, and swing connections.

Anchor Details: Detail fabrication of each anchor indicated. Show dimensions and methods of assembly and attachment to building structure.

Alignment Guide Details: Detail field assembly and attachment to building structure.

Schedule: Indicate type, manufacturer's number, size, material, pressure rating, end connections, and location for each expansion joint.

INFORMATIONAL SUBMITTALS

Welding certificates.

Product Certificates:  For each type of expansion joint, from manufacturer.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: Include a copy of each approved submittal along with any applicable maintenance data in the project operation and maintenance manual.

QUALITY ASSURANCE

Welding Qualifications:  Qualify procedures and personnel according to the following:

AWS D1.1/D1.1M, "Structural Welding Code - Steel."

ASME Boiler and Pressure Vessel Code:  Section IX.

WARRANTY/GUARANTEE

See Division 23 Specification Section “Basic Mechanical Requirements – HVAC” for warranty and guarantee requirements.

PRODUCTS

GENERAL PRODUCT REQUIREMENTS

### Equipment Design and Selection: Expansion fittings, anchors, guides and loops shall be designed and selected, for the intended use, in accordance with the scheduled capacities on the drawings and the requirements of this specification.

Acceptable Manufacturers: Subject to compliance with requirements, provide expansion fittings, joints, and guides by one (1) of the following:

Expansion Joints :

Adsco Manufacturing LLC.

Metraflex Inc.

Tozen Corp.

Vibration Mountings.

Alignment Guides:

Advanced Thermal Systems Inc.

Grinnell Corp.

Metraflex Inc.

PACKLESS EXPANSION JOINTS

Metal-Bellows Packless Expansion Joints:<Select type expansion joint for project>

Standards: ASTM F 1120 and EJMA's "Standards of the Expansion Joint Manufacturers Association, Inc."

Type:  Circular, corrugated bellows with external tie rods.

Minimum Pressure Rating:  175 psig.

Expansion Joints for Copper Tubing: Two (2) ply phosphor-bronze bellows, copper pipe ends, and brass shrouds.

End Connections for Copper Tubing two (2) and Smaller:  Solder joint or threaded.

End Connections for Copper Tubing two and one half (2-1/2) to four (4) inches:  Solder joint or threaded.

End Connections for Copper Tubing five (5) inches and Larger:  Flanged.

Rubber Packless Expansion Joints:

Standards:  ASTM F 1123 and FSA's "Technical Handbook:  Non-Metallic Expansion Joints and Flexible Pipe Connectors."

Material:  Fabric-reinforced rubber complying with FSA-NMEJ-703.

Spherical Type:  Single or double spheres with external control rods.

Minimum Pressure Rating: 175 psig at 240°F.

Material for Water:  Butyl rubber.

End Connections: Full-faced, integral steel flanges with steel retaining rings drilled to match flange bolt holes over entire surface of flanges.

Expansion Compensator expansion Joint:

Standards: ASTM F 1123 and FSA's "Technical Handbook:  Non-Metallic Expansion Joints and Flexible Pipe Connectors."

Type:  Two (2) ply phosphor bronze bellows, brass shrouds, and end fittings for copper piping systems and two (2) ply stainless-steel bellows, carbon-steel shrouds, and end fittings for steel piping systems.  Include internal guides, antitorque device, and removable end clip for proper positioning.

Minimum pressure rating: for 60 psig minimum for pressure systems and for 175 psig minimum for high-pressure systems.

ALIGNMENT GUIDES AND ANCHORS

Alignment Guides:

Description: Steel, factory-fabricated alignment guide, with bolted two (2) section outer cylinder and base for attaching to structure; with two (2) section guiding spider for bolting to pipe.

Anchor Materials:

Steel Shapes and Plates:  ASTM A 36/A 36M.

Bolts and Nuts:  ASME B18.10 or ASTM A 183, steel hex head.

Washers:  ASTM F 844, steel, plain, flat washers.

Mechanical Fasteners:  Insert-wedge-type stud with expansion plug anchor for use in hardened portland cement concrete, with tension and shear capacities appropriate for application.

Stud:  Threaded, zinc-coated carbon steel.

Expansion Plug:  Zinc-coated steel.

Washer and Nut:  Zinc-coated steel.

Chemical Fasteners: Insert-type-stud, bonding-system anchor for use with hardened portland cement concrete, with tension and shear capacities appropriate for application.

Bonding Material: ASTM C 881/C 881M, Type IV, Grade 3, two (2) component epoxy resin suitable for surface temperature of hardened concrete where fastener is to be installed.

Stud: ASTM A 307, zinc-coated carbon steel with continuous thread on stud unless otherwise indicated.

Washer and Nut:  Zinc-coated steel.

EXECUTION

EXPANSION-JOINT INSTALLATION <Designer shall locate expansion compensators and loops or drawings>

Install expansion joints of sizes matching sizes of piping in which they are installed.

Install metal-bellows expansion joints according to EJMA's "Standards of the Expansion Joint Manufacturers Association, Inc."

Install rubber packless expansion joints according to FSA-NMEJ-702.

PIPE LOOP AND SWING CONNECTION INSTALLATION

Install pipe loops cold-sprung in tension or compression as required to partly absorb tension or compression produced during anticipated change in temperature.

Connect risers and branch connections to mains with at least five (5) pipe fittings including tee in main.

Connect risers and branch connections to terminal units with at least four (4) pipe fittings including tee in riser.

Connect mains and branch connections to terminal units with at least four (4) pipe fittings including tee in main.

ALIGNMENT GUIDE AND ANCHOR INSTALLATION<Designer shall locate pipe anchors on drawings>

Install alignment guides to guide expansion and to avoid end-loading and torsional stress.

Install guide(s) on each side of pipe expansion fittings and loops.  Install guides nearest to expansion joint not more than pipe diameters from expansion joint.

Attach guides to pipe and secure guides to building structure.

Install anchors at locations to prevent stresses from exceeding those permitted by ASME B31.9 and to prevent transfer of loading and stresses to connected equipment.

Anchor Attachments:

Anchor Attachment to Black-Steel Pipe:  Attach by welding.  Comply with ASME B31.9 and ASME Boiler and Pressure Vessel Code:  Section IX, "Welding and Brazing Qualifications."

Anchor Attachment to Galvanized-Steel Pipe:  Attach with pipe hangers.  Use MSS SP-69, Type 42, riser clamp welded to anchor.

Anchor Attachment to Copper Tubing:  Attach with pipe hangers.  Use MSS SP-69, Type 24, U-bolts bolted to anchor.

Fabricate and install steel anchors by welding steel shapes, plates, and bars.  Comply with ASME B31.9 and AWS D1.1/D1.1M.

Anchor Attachment to Steel Structural Members:  Attach by welding.

Anchor Attachment to Concrete Structural Members:  Attach by fasteners.  Follow fastener manufacturer's written instructions.

Use grout to form flat bearing surfaces for guides and anchors attached to concrete.

END OF SECTION 230516